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· Features
■ Applications
 •  AC/DC desktop type power unit
•  High efficiency
•  Universal AC input / Full range(90-264V~)
•  Built- in active PFC function
 • High frequency switching mode
 •  Protection: Short circuit / Over voltage /Over temperature
 • Display voltage、current
•  1 years warranty

•  IT equipment or Radio system
•  Machine room
•  Surveillance system
•  Home appliances
· Mode Encoding 
      G600-XXXYYY
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® When using CAN communication

Pin No. Assignment
1 CANH
2 5V+
3 CANL
4 5V-

® When using RS485 communication

Pin No. Assignment
CAN & RS485
interface 1 RS485-8
2 5V+
3 RS485-A
4 5V-
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MODEL�
G600-240200�
G600-360160�
G600-420142�
G600-480125�
G600-600100�
�
OUTPUT�
Voltage   �
24V±5%�
36V±5%�
42V±5%�
48V±5%�
60V±5%�
�
�
current �
0-20A�
0-16A�
0-14.2A�
0-12.5A�
0-10A�
�
�
Rated power�
480W�
576W�
596.4W�
600W�
600W�
�
�
Voltage regulation�
1%�
�
�
Load regulation�
5%�
�
�
Start-up time�
1000mS(Input:115VAC  Output: Full load)�
�
�
Rise time�
30mS (Input:115VAC  Output: Full load)�
�
�
Hold time�
15mS (Input:115VAC  Output: Full load)�
�
�
Ripple voltage�
<output voltage*1% (20MHz ，AC coupling mode, connected in parallel with 0.1uf ceramic capacitor and 47uf electrolytic capacitor)�
�
�
LCD display�
Display voltage(Display error ± 2%), current(Display error ± 6%),�
�
INPUT�
Rated input voltage�
100 - 240VAC  50 / 60Hz�
�
�
Input voltage range Note.2�
90 - 264VAC �
�
�
Power factor (Typ.)�
PF>0. 98  @AC100V,Full load�
�
�
Input current (Typ.)�
6.8A@100VAC		�
�
�
Inrush current  (Typ.)�
75A/230VAC (cold start)�
�
�
Standby input power �
<5W�
�
�
Efficiency (Typ.)�
91%�
92%�
92%�
92%�
93%�
�
PROTECTION�
Short circuit 	�
Protection type : Shut down output�
�
�
Over voltage�
Protection type : Shut down output�
�
�
Over current�
Protection type : Shut down output  (110-160%)�
�
�
Over temperature �
Protection type : Shut down output�
�
ENVIRONMENT�
Working temperature �
-10 - +40℃ (Refer to " Derating Curve")�
�
�
Working humidity�
0 - 90% RH �
�
�
Storage temperature, humidity�
-40 - +70℃, 0 - 95% RH �
�
�
Cooling�
 Natural convection�
�
�
Vibration resistance�
10-50Hz,2G10min.1cycle,60min.eachalongX,Y,Zaxes�
�
SAFETY&EMC （Note.3）�
Max. temperature rise�
< 40℃ on casing�
�
�
Hi-Pot Insulation�
i/p to o/p: 3000V (1 min)�
�
�
Safety standards�
IEC62368-1�
�
�
EMC Emission�
Parameter�
Standard�
Test Level I Note�
�
�
�
Conducted�
EN55032 FCC PART15�
Class B�
�
�
�
Radiated�
EN55032 FCC PART15�
Class B�
�
�
�
Harmonic Current�
EN61000-3-2�
.....�
�
�
�
Voltage Flicker�
EN61000-3-3�
.....�
�
�
EMC IMMUNITY�
EN61000-4-2，EN61000-4-3，EN61000-4-4，EN61000-4-5，EN61000-4-6，EN61000-4-8，EN61000-4-11�
�
OTHERS�
MTBF�
30000H�
�
�
Dimension�
240*117*66mm (L*W*H)�
�
�
Weight�
1500g�
�
NOTE�
All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature.


Derating may be needed under low input voltages. Please check the derating curve for more details.


The power unit is considered as an independent unit, but  the final equipment still need to re-confirm that the whole system complies with the EMC directives. �
�
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Block Diagram
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Derating Curve





Static Characteristics
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LCD display 
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